CHARGING STATION eMH1

1W1101

Wall-mounted charging station for charging electric vehicles according to IEC 61851-1 Mode 3, with the following functions and technical features:

Charging station for wall installation, 3-phase supply connection to the local electricity grid up to overvoltage category III with 230/400 V, 16 A, 50 Hz for a maximum charging capacity of 11 kW, MCB required onsite. Integrated charging cable with type 2 connector acc. to IEC62196-2.

Compact, elegant housing for installation in protected outdoor areas and indoors, made from ABS plastic, IP54 degree of protection, with RAL 9005 enamel paint. With lockable front cover shield made of UV-resistant ASA plastic, painted to RAL 9006, for limited access to the integrated RCCB.

Setup and customization via internal RS485 interface, electric shock protection through welding detection, internal RCCB type A 30 mA and additionally integrated DC fault current detection. Adjustment of charging power through integrated temperature monitoring and phase current measurement. Operating status and potential errors displayed via LED indicators at the top of the housing.

Includes instruction manual, two keys for the cover shield, mounting set as well as a drilling template for installation. Pre-assembled ready for grid connection and individually checked.

Power supply			230/400 V, 16 A / 50 Hz

Supply cable size		5 x 6 mm²

Upstream fuse			required onsite (16 A, C characteristic)

Connection system		single charging cable with type 2 connector in acc. with IEC62196-2,

length approx. 6,35 m

Charging capacity		11 kW

RCCB 				residual current circuit breaker type A, 30 mA

DC fault current detector	electronic, I delta n d.c. ≥ 6 mA

Installation contactor		4-pole (charging procedure activation)

Welding Detection		Triggering on welding of the contactor

Temperature monitoring	Stepped lowering of the charging current in the event of overheating

Charge controller		EVCC2

Display				LED indicators for operating, error and RFID status

Interface			RS485

Class of protection		I

Overvoltage category		III

Dimensions (net)		272 x 221 x 116 mm (H x W x D)

Dimensions (packaging)	330 x 320 x 260 mm (H x W x D)

Packaging unit (PU) 		1 unit

Operating temperature		-30 to 85°C (storage), -30 to 50°C (operation)

Relative humidity		5 to 95% (no condensation)

Weight				approx. 4.500 g

Type 				wall-mounted housing

Material			plastic

Color 				housing: enamel paint, RAL9005; cover shield: enamel paint, RAL9006

Manufacturer			ABL SURSUM

Model				eMH1

Product number		1W1101

EAN-Code			4011721175386

Quantity			………………… units

Delivery cost:			………………… €/unit

Installation/Setup cost:		………………… €/unit

UP				………………… €/unit

Total: 				………………… €